## Slide 1
The Psychrometric Chart
HVAC's master diagram — and the missing tool in most Building Management Systems
Why equipment designers cannot work without it, why traditional BMS never adopted it, and how this one chart answers ASHRAE 55, 62.1, 90.1 and Guideline 36 at the same time.
Moist-air states
Design tool
ASHRAE-aligned
Live controls

## Slide 2
START HERE
Who uses this chart — and on what equipment
Long before a building is controlled, someone has to choose the machines that condition its air. Those people live on the psychrometric chart.
Who they are
“HVAC equipment designers” are the mechanical engineers who select and size air-conditioning equipment:
• manufacturers' application engineers
• consulting / design engineers
• commissioning engineers who prove it works
What “HVAC equipment” means
The machines that actually change the air:
• air-handling units (AHUs) and their heating / cooling coils
• mixing & economizer dampers
• humidifiers and dehumidifiers
• energy-recovery wheels (ERV / HRV)
• chillers and DX systems, fans, VAV terminals
What they must decide
• How much cooling or heating is needed
• How much of that cooling removes MOISTURE rather than heat
• How big the coil must be
• How much outside air to mix in
• Whether condensation or coil freezing will occur
Every one of those decisions is a point or a line on the psychrometric chart. That is why the chart — not the equipment catalogue — is where air-conditioning design actually happens.

## Slide 3
WHY IT EXISTS
Why designers cannot work without it
Air conditioning is not simply “making air colder”. It is moving MOIST AIR from one state to another — and the psychrometric chart is the map of every state air can be in.
Every process is a line
Cooling, heating, humidifying, dehumidifying and mixing each move the air in a characteristic direction. Draw the line and you have described the process.
Capacity comes from the chart
The energy content (enthalpy) at each end of the line, multiplied by airflow, is the kW the coil must deliver. That is how equipment gets sized.
Sensible vs latent
The chart separates cooling that lowers temperature from cooling that removes water. The two behave differently and must be sized separately.
Physical limits are visible
The curved boundary is 100% humidity — air cannot go beyond it. It shows where condensation begins and where a coil would freeze.

## Slide 4
HOW TO READ IT
One dot is the state of the air
100% RH
(saturation)
Comfort zone (ASHRAE 55)
OA
RA
MA
SA
Dry-bulb temperature →
↑ Moisture in the air
OA outside air · RA return air from the rooms · MA the mixture entering the coil · SA supply air delivered to the rooms.
Dashed green = mixing; solid blue = the cooling coil.
1
Two axes fix everything
Across is temperature; up is the actual weight of water the air carries. Pin both and the air's state is pinned — relative humidity, dew point, wet-bulb and energy content all follow from that one dot.
2
The curve is a hard limit
It marks 100% humidity — air can never sit above it. Drive the dot onto the curve and water comes out: the dew point, a wet coil, a fogged window.
3
Mixing is a straight line
Outside and return air blend to a point on the line joining them. How far along it sits gives the proportion: a third of the way from RA means a third outside air.
4
A coil pulls down and left
Left removes temperature (sensible heat); down removes water (latent heat). The slope of MA→SA is the split — and that split is what sizing a coil actually means.
5
Comfort is an area
The acceptable range of temperature and humidity is drawn straight onto the chart. Supply air must be chosen so the room lands inside that box, not merely at the right temperature.
6
Faults show as bad geometry
If the mixed-air dot is not on the line between outside and return air, something is lying — a stuck damper or a drifting sensor. The picture catches what alarm limits miss.

## Slide 5
THE GAP
Why traditional BMS never adopted the chart
Controls think in single numbers
A BMS is assembled from loops that each watch ONE value — a temperature, a pressure. A state point needs two readings judged together; classic controls had no concept of a two-dimensional air state.
The sensors often aren't there
You need temperature AND humidity at the same place. Many units measure only dry-bulb on outside, mixed and return air — extra humidity sensors mean extra cost, wiring and calibration drift.
The maths was too expensive
Moisture content and energy content are non-linear and depend on barometric pressure. Older controllers had very little memory and no floating-point maths, so psychrometrics were left out.
Graphics couldn't draw it
Early front-ends drew simple equipment schematics and time-series trends. A live chart with curves and overlays needs real rendering — so the chart stayed a static page in the design binder.
Design and operations are separate worlds
The chart is used once, offline, to select equipment. What is handed to the controls contractor is a list of setpoints — not the physics behind them. The reasoning is lost at handover.
The simpler option was allowed
Codes permit dry-bulb-only economizer switching, so designs avoided humidity sensing that was historically unreliable. The easier, compliant path quietly became the default.
The consequence
Operators end up diagnosing a TWO-DIMENSIONAL problem — heat AND moisture — by staring at separate one-dimensional trend lines. The information is there; the picture is not.

## Slide 6
THE RULEBOOKS
Four ASHRAE standards, in one line each
ASHRAE 55
Comfort
Will people feel comfortable?
ASHRAE 62.1
Fresh air
Is there enough outside air to stay healthy?
ASHRAE 90.1
Energy
Are we doing it without wasting energy?
Guideline 36
The referee
How should the equipment be run to hit all three?
Comfort and fresh air push toward MORE conditioning; energy pushes toward LESS. Guideline 36 is the rulebook that settles the argument.

## Slide 7
THE BIG IDEA
One sheet — every rulebook draws on it
The psychrometric chart
temperature × moisture — the only two axes
Every requirement around it becomes a shape on THESE SAME AXES.
ASHRAE 55 draws an AREA
The comfort zone: the band of temperature and humidity occupants accept. The air-side of the standard becomes a region you must land the room inside.
ASHRAE 62.1 draws a POINT ON A LINE
The required outside-air fraction fixes exactly where the mixed-air dot must sit along the line between return and outside air.
ASHRAE 90.1 draws a DIRECTION
Lines of equal energy content show when outside air is the cheaper source, and how far the dot may be pushed before energy is thrown away.
Guideline 36 draws the PATH
The sequences are the route the dot travels through the day — economizer, coil, setpoint reset — from outside air to the room.
Read this the right way round
The chart is not the small overlap left where four standards happen to agree. It is the COMMON SHEET they are all drawn on — an area, a line, a direction and a path, sharing one pair of axes. Satisfy all four and the shapes simply fit together.

## Slide 8
HOW IT SATISFIES EACH
One dot on the chart answers every question
55 — Comfort
The comfort zone is drawn straight onto the chart. Is the room dot inside the acceptable temperature/humidity band — and if not, which way is it off?
62.1 — Fresh air
The mixed-air dot must sit on the line between return and outside air. Its position along that line IS the outside-air proportion.
90.1 — Energy
Equal-energy lines reveal free cooling: when outside air holds less energy than return air, the economizer can meet the load with no mechanical cooling.
G36 — Sequences
Visible proof the sequences land the dot inside the comfort zone, on the correct fresh-air line, along the lowest-energy path.
In one sentence: plot where the air IS, see where it MUST be, how it gets there, and whether it does so at least energy.

## Slide 9
THE DIFFERENCE
Trend-based BMS vs a psychrometric-aware BMS
QUESTION BEING ASKED
TREND-BASED BMS (TODAY)
PSYCHROMETRIC-AWARE BMS
What the operator sees
Several separate trend lines, read one at a time
One picture showing the air's actual state
Is the outside-air mix right?
Inferred from the damper command
The mixed-air dot must fall on the outside–return line
Can we free-cool right now?
Usually temperature-only, so humid-but-cool and dry-but-warm hours are misjudged
Decided on true energy content of the air
Humidity control
A separate loop, often fighting the cooling loop
Heat and moisture handled as one state
Finding faults
Alarm limits on individual points
The shape of the process line exposes coil, damper and sensor faults
Proving the standards
Checked manually, usually after the fact
Comfort, ventilation and energy judged together, live
None of this needs new field equipment beyond humidity sensing on the air streams — the difference is what the software does with readings the building is already taking.

## Slide 10
One chart. Four rulebooks.
The psychrometric chart is not a design-only artifact. Bringing it into the building's controls turns anonymous setpoints back into visible physics — and puts comfort, air quality and energy into a single picture an operator can read at a glance.
The computing power to draw it live has been ordinary for years. What has kept the chart out of the control room is habit and missing humidity sensors — not physics, and no longer technology.